TRANE

| TR200 SPEED DRIVE START UP SHEET |
| --- |
| WORK ORDER NO. |  | DRIVE NO. |  | TECHNICIANS INITIALS |  |
| JOB NAME: |  | SERIAL NUMBER |  |
| DRIVE MAKE: | Trane | MODEL NUMBER |  |

Note: Ensure parameter 0-03 is set to North America.

# Text boxes

| Drive | Input amps | Output amps |
| --- | --- | --- |
| Speed | A1 | A2 | A3 | A1 | A2 | A3 |
| 100% |  |  |  |  |  |  |

VFD Display amps: /                  / Display frequency: /        60        HZ

| VFD input voltage | VFD output voltage to motor |
| --- | --- |
| L1 – L2 | L1 – L3 | L2 – L3 | U-V | U-W | V-W |

| BYPASS SECTION (If so equipped) |
| --- |
| Overload Calibrated |  | AMPS |  |
| Voltage Reading at Output of Overload Block |  |

| MOTOR DATA |
| --- |
| Make |  |
| Voltage |  |
| Phase | 3 |
| F.L.A |  |
| HP |  |
| RPM |  |
| S.F. |  |

MOTOR ROTATION CHECK:

__   IN VFD MODE

__ BYPASS MODE

| No. | Parameter Description |  |
| --- | --- | --- |
| 540.0 | Relay 1, Output Function (No Alarm) |  |
| 540.1 | Relay2, Output Function (Running) |  |
| 541.0 | Relay on Delay (.01 sec) |  |
| 542.0 | Relay off Delay (2 sec) |  |
| 600 | Live Zero Time (10 sec) |  |
| 601 | Function After Time Out (No Function) |  |
|  | Terminal 53, A/I Voltage (Reference 1.) |  |
| 610 | Terminal 53, Min. Scaling (0.0 V) |  |
| 611 | Terminal 53 Max. Scaling (10.0 V) |  |
| 617 | Live Zero (Enabled AI 53) |  |
|  | Terminal 54, A/I Voltage (feedback.) |  |
| 620 | Terminal 54, Min. Scaling (0.0 V) |  |
| 621 | Terminal 54 Max. Scaling (10.0 V) |  |
| 627 | Live Zero (Enabled AI 54) |  |
| 650 | Terminal 42, Output (Output Frequency) |  |
|  | Additional setup required if embedded bacnet is used. Par 830 (bacnet). |  |
|  | Instance |  |
| 1420 | Reset Functions (set to infinite auto) |  |
| 1540 | Nameplate: Unit Type |  |
| 1541 | Nameplate: Power Component |  |
| 1546 | Nameplate: TR200 Order No. |  |
| 1543 | Nameplate: Software Version |  |
| NOTE: If (6) or (8) pole motors are being used additional adjustments to motor parameter for cosphi may be required. |
| NOTE: RE P412: 6 Hz on fans 18 Hz on Pumps Same for P302: 23 Hz on Intellipak |

| No. | Parameter Description |  |
| --- | --- | --- |
| 121 | Motor Power |  |
| 122 | Motor Voltage |  |
| 123 | Motor Frequency |  |
| 124 | Motor Current |  |
| 125 | Rated Motor Speed |  |
| 129 | Automatic Motor Adaptation, AMA |  |
| 173 | Flying Start (Fans=Enable, Pumps=Disable) |  |
| 180 | FUNCTION @ STOP (Coast) |  |
| 182 | MIN SPEED FUNCTION @ STOP (6Hz for fan or 18Hz for pump) |  |
| 302 | Minimum Reference (20 Hz or required speed by application) |  |
| 303 | Maximum Reference |  |
| 341 | Ramp-up Time (Fans=20 - 120 sec, Pumps=10 sec.) |  |
| 342 | Ramp-down Time)(as per par 341) |  |
|  | (See notes below re p510-542) |  |
| 412 | Output Frequency Low Limit |  |
| 414 | Output Frequency High Limit |  |
| 416 | Torque Limit (160%) |  |
| 418 | Current Limit (110% of motor FLA) |  |
| 451 | Warning: High Current, I |  |
| 510 | Terminal 18 D/I (Run/Stop) |  |
| 511 | Terminal 19 D/I (No Operation) |  |
| 512 | Terminal 27 D/I (Safety Interlock) |  |
| 513 | Terminal 29 D/I (Jog) |  |
| 514 | Terminal 32 D/I (No operation) |  |
| 515 | Terminal 33 D/I (No operation) |  |
| Note: | P502 (output) P511 (run permissive) | If bypass |

Note: If drive has integrated bypass installed leave par. 510 through 542 at factory settings. Refer to field wiring print.

(	Program Uploaded to LCP Display	Commissioning Date ____ _______________________

Owners Rep Signature_______________________      Trane Tech Signature___________________________